## BCMU(control box) CAN protocol
Explain: 1、Use CAN2.0 extended frame communication mode，and the communication baud rate is 500kbps. 2、For 16-bit(word) or 32-bit(long) data types，the low byte at the front and high byte at the rear. For example1,the total voltage of battery modules(16-bit)=((u16)data[3]<<8)¦data[2],data[2] is low (8-bit),data[3] is high (8-bit). For example2,charge and discharge times of battery modules(32位)=((u32)data[5]<<24)¦((u32)data[4]<<16)¦((u32)data[3]<<8)¦data[2],data[2] is low (8-bit),data[3] is secondly low (8-bit),data[4] is secondly high (8-bit),data[5] is the highest (8-bit).
Domain of Frames ID(Hex) |  |  |  | Domain of Frames Data(front←→back) | [7 empty] | Frame Length | Explain
bit28-24 | bit23-16 | bit15-8 | bit7-0 | data[0] | data[1] | data[2] | data[3] | data[4] | data[5] | data[6] | data[7] | length
Head of ID | Sourc Address | Destination Address | Tail of ID | Data Identification |  | Data Definition
0x0c | 0x50 | 0xff | 0x32 | 0x43 | 0x00 | Battery protection status |  | Battery modules working status |  | Battery modules charge and discharge status |  | 8 | Unsigned number of 16-bit, see details in "data format"
|  |  | 0x33 | 0xc3 | 0x00 | Output IO state |  | Input IO state |  | 0x00 for reserve |  | 8 | Show by bit,see details in"IO status"
|  |  | 0x34 | 0x43 | 0x00 | Battery string external alarm information 0 |  | Battery string external alarm information 1 |  | Battery string internal alarm information 0 |  | 8 | Show by bit,see details in "alarm bits"
|  |  |  | 0x81 | 0x03 | Battery string internal alarm information 1 |  | \ | \ | \ | \ | 4
|  |  | 0x35 | 0x43 | 0x00 | Battery string external fault information 0 |  | Battery string external fault information 1 |  | Battery string internal fault information 0 |  | 8 | Show by bit,see details in "fault bits"
|  |  |  | 0x81 | 0x03 | Battery string internal fault information 1 |  | \ | \ | \ | \ | 4
|  |  | 0x50 | 0x43 | 0x00 | the total voltage of battery string |  | Output current of battery string |  | Output power of battery string |  | 8 | 16-bit signed number,see details in "data format"
|  |  |  | 0x83 | 0x03 | SOC of battery string |  | SOH of battery string |  | Average temperature of battery string |  | 8
|  |  | 0x51 | 0x43 | 0x00 | The number of minimum voltage cell in battery string |  | The cell minimum voltage in battery string |  | 0x00 for reserve |  | 8
|  |  |  | 0x83 | 0x03 | The number of maximum voltage cell in battery string |  | The cell maximum voltage in battery string |  | 0x00 for reserve |  | 8
|  |  | 0x52 | 0x43 | 0x00 | The number of minimum temperature in the battery string |  | The minimum temperature in battery string |  | 0x00 for reserve |  | 8
|  |  |  | 0x83 | 0x03 | The number of maximum temperature in the battery string |  | The maximum temperature in the battery string |  | 0x00 for reserve |  | 8
|  |  | 0x53 | 0x41 | 0x00 | Charge and discharge times of battery string |  |  |  | \ | \ | 6 | 32-bit unsigned number,see details in "data format"
|  |  |  | 0x01 | 0x01 | Remain energy of battery string |  |  |  | \ | \ | 6
|  |  |  | 0x01 | 0x02 | Total capacity of battery string |  |  |  | \ | \ | 6
|  |  |  | 0x01 | 0x03 | 0x00 for reserve |  |  |  | \ | \ | 6
|  |  |  | 0x01 | 0x04 | 0x00 for reserve |  |  |  | \ | \ | 6
|  |  |  | 0x01 | 0x05 | History accumulates charge capacity of battery string |  |  |  | \ | \ | 6
|  |  |  | 0x01 | 0x06 | History accumulates discharge capacity of battery string |  |  |  | \ | \ | 6
|  |  |  | 0x01 | 0x07 | History accumulates charge energy of battery string |  |  |  | \ | \ | 6
|  |  |  | 0x81 | 0x08 | History accumulates discharge energy of battery string |  |  |  | \ | \ | 6
|  |  | 0x59 | 0x43 | 0x00 | The sampling total voltage of battery string |  | 0x00 for reserve |  | 0x00 for reserve |  | 8 | 16-bit signed number,see details in "data format"
|  |  | 0x5a | 0x43 | 0x00 | The max. charge current of battery string(charge current limits) |  | The max. discharge current of battery string(discharge current limits) |  | The max. charge power of battery string(charge power limits) |  | 8 | 16-bit unsigned number,see details in "data format"
|  |  |  | 0x81 | 0x03 | The max. discharging power of battery string(discharge power limits) |  | \ | \ | \ | \ | 4
0x09 | 0xe0 | 0xff | 0xff | 0x01 | 0x02 | 0x00 | 0x00 | 0x00 | 0x00 | 0x00 | 0x00 | 8 | Reset Command

## SN-NC Protocol
Explain: 1、Use CAN2.0 extended frame communication mode，and the communication baud rate is 500kbps.
ESO TO BMS reqest for SN and NC
Domain of Frames ID(Hex) |  | Domain of Frames Data(front←→back) | [7 empty] | Frame Length | Explain
|  | data[0] | data[1] | data[2] | data[3] | data[4] | data[5] | data[6] | data[7] | length
Data Definition
0xff |  | 0xaa | 0x55 | \ | \ | \ | \ | \ | \ | 2 | Inquire for SN and NC / Charging History
BMS TO ESO reply with: SN / NC / historical charging
Domain of Frames ID(Hex) |  | Domain of Frames Data(front←→back) data[0]: Domain of Frames Data(front←→back) | Frame Length | Explain
|  | data[0] | data[1] | data[2] | data[3] | data[4] | data[5] | data[6] | data[7] | length
Data Definition
0x500 |  | SN byte0 | SN byte1 | SN byte2 | SN byte3 | SN byte4 | SN byte5 | SN byte6 | SN byte7 | 8 | Battery 1 SN
0x501 |  | SN byte8 | SN byte9 | SN byte10 | SN byte11 | SN byte12 | SN byte13 | SN byte14 | SN byte15 | 8
0x502 |  | SN byte16 | SN byte17 | SN byte18 | SN byte19 | \ | \ | \ | \ | 4
0x503 |  | NC byte0 | NC byte1 | NC byte2 | NC byte3 | Charging History byte0 | Charging History byte1 | Charging History byte2 | Charging History byte3 | 8 | NC and Charging history
0x510 |  | SN byte0 | SN byte1 | SN byte2 | SN byte3 | SN byte4 | SN byte5 | SN byte6 | SN byte7 | 8 | Battery 2 SN
0x511 |  | SN byte8 | SN byte9 | SN byte10 | SN byte11 | SN byte12 | SN byte13 | SN byte14 | SN byte15 | 8
0x512 |  | SN byte16 | SN byte17 | SN byte18 | SN byte19 | \ | \ | \ | \ | 4
0x513 |  | NC byte0 | NC byte1 | NC byte2 | NC byte3 | Charging History byte0 | Charging History byte1 | Charging History byte2 | Charging History byte3 | 8 | NC and Charging history
0x520 |  | SN byte0 | SN byte1 | SN byte2 | SN byte3 | SN byte4 | SN byte5 | SN byte6 | SN byte7 | 8 | Battery 3 SN
0x521 |  | SN byte8 | SN byte9 | SN byte10 | SN byte11 | SN byte12 | SN byte13 | SN byte14 | SN byte15 | 8
0x522 |  | SN byte16 | SN byte17 | SN byte18 | SN byte19 | \ | \ | \ | \ | 4
0x523 |  | NC byte0 | NC byte1 | NC byte2 | NC byte3 | Charging History byte0 | Charging History byte1 | Charging History byte2 | Charging History byte3 | 8 | NC and Charging history
0x530 |  | SN byte0 | SN byte1 | SN byte2 | SN byte3 | SN byte4 | SN byte5 | SN byte6 | SN byte7 | 8 | Battery 4 SN
0x531 |  | SN byte8 | SN byte9 | SN byte10 | SN byte11 | SN byte12 | SN byte13 | SN byte14 | SN byte15 | 8
0x532 |  | SN byte16 | SN byte17 | SN byte18 | SN byte19 | \ | \ | \ | \ | 4
0x533 |  | NC byte0 | NC byte1 | NC byte2 | NC byte3 | Charging History byte0 | Charging History byte1 | Charging History byte2 | Charging History byte3 | 8 | NC and Charging history
0x540 |  | SN byte0 | SN byte1 | SN byte2 | SN byte3 | SN byte4 | SN byte5 | SN byte6 | SN byte7 | 8 | Battery 5 SN
0x541 |  | SN byte8 | SN byte9 | SN byte10 | SN byte11 | SN byte12 | SN byte13 | SN byte14 | SN byte15 | 8
0x542 |  | SN byte16 | SN byte17 | SN byte18 | SN byte19 | \ | \ | \ | \ | 4
0x543 |  | NC byte0 | NC byte1 | NC byte2 | NC byte3 | Charging History byte0 | Charging History byte1 | Charging History byte2 | Charging History byte3 | 8 | NC and Charging history
0x550 |  | SN byte0 | SN byte1 | SN byte2 | SN byte3 | SN byte4 | SN byte5 | SN byte6 | SN byte7 | 8 | Battery 6SN
0x551 |  | SN byte8 | SN byte9 | SN byte10 | SN byte11 | SN byte12 | SN byte13 | SN byte14 | SN byte15 | 8
0x552 |  | SN byte16 | SN byte17 | SN byte18 | SN byte19 | \ | \ | \ | \ | 4
0x553 |  | NC byte0 | NC byte1 | NC byte2 | NC byte3 | Charging History byte0 | Charging History byte1 | Charging History byte2 | Charging History byte3 | 8 | NC and Charging history
0x560 |  | SN byte0 | SN byte1 | SN byte2 | SN byte3 | SN byte4 | SN byte5 | SN byte6 | SN byte7 | 8 | Battery Stack / Controller SN
0x561 |  | SN byte8 | SN byte9 | SN byte10 | SN byte11 | SN byte12 | SN byte13 | SN byte14 | SN byte15 | 8
0x562 |  | SN byte16 | SN byte17 | SN byte18 | SN byte19 | \ | \ | \ | \ | 4
0x563 |  | NC byte0 | NC byte1 | NC byte2 | NC byte3 | Charging History byte0 | Charging History byte1 | Charging History byte2 | Charging History byte3 | 8 | NC and Charging history
SN - Serial number | (ASCII)
NC - Number of cycles | unit: cycle
Charging history | unit: 0.1kwh

## data format
Data Name | Range & Explain | Dimension | Note
Battery protection status | 0:Normal正常； 1:Charge stop充电截止； 2:Discharge stop放电截止； 3:Ask for standby请求待机； 4:Ask for protect请求保护； | NA | PCS/中控必须监控,0:充放电设备可以充电和放电 1:只可以放电 2:只可以充电 3:不能充电和放电 4:充放电设备停机切断直流端（BMS断开接触器） PCS/Inverter/DCDC-controler should follow this: If this byte is 0, the battery can be discharged & charged; If this byte is 1, the battery can be discharged and can't be charged, the PCS/Inverter/DCDC-controler should stop charge output; If this byte is 2, the battery can be charged and can't be discharged, PCS/Inverter/DCDC-controler should stop discharge; If this byte is 3, the battery can't be discharged & charged, PCS/Inverter/DCDC-controler should stop discharge & charge; If this byte is 4, the relaies/contactors in the battery control box will turn off and the battery string will disconnect to the PCS/Inverter/DCDC-controler
Working status | 0:Initializing初始化； 1:Stop停止； 2:Starting正在启动； 3:Running运行； 4:Stopping； 5:Fault； | NA | 建议PCS/中控监控，3:充放电设备允许启动和充放电 其它值:充放电设备必须停机关闭充放电（BMS故障或接触器未闭合） PCS/Inverter/DCDC-controler should follow this: If this byte is 3, the battery can be discharged & charged, and if it is the other data the PCS/Inverter/DCDC-controler must stop power output(the relaies/contactors in the battery control box is cutoff)
charge/discharge status | 0:Idle空闲； 1:Charge充电； 2:Discharge放电； | NA | 建议PCS/中控监控；
Battery string total voltage | [0,10000] | 0.1V
Battery output current | [-30000,30000] | 0.1A | '-' represents charging
Battery output power | [-30000,30000] | 0.1kW | '-' represents charging
SOC | [0,1000] | 0.1%
SOH | [0,1000] | 0.1%
Cell voltage | [0,5000] | 0.001V | It's suitable for display the Max. / Min. cell voltage
Temperature | [-40,130] | 1℃ | It's suitable for display the cell Max. / Min. / Average temperature
Battery remain energy | [0,2000000] | 1Wh
Battery total energy | [1,500000] | 1mAH
Can be charged energy | [0,20000] | 0.1kWh
Can be discharged energy | [0,20000] | 0.1kWh
History accumulates charge capacity of battery string | [0,+] | 1AH
History accumulates discharge capacity of battery string | [0,+] | 1AH
History accumulates charge energy of battery string | [0,+] | 0.1kWh
History accumulates discharge energy of battery string | [0,+] | 0.1kWh
Charge current limits | [0,50000] | 0.1A | PCS/中控必须监控；0:禁止充电,非0:充放电设备充电电流不能超过该值 if it's '0', the battery string can't be charged and if other data is the max. charge current that the battery can be accepted
Discharge current limits | [0,50000] | 0.1A | PCS/中控必须监控；0:禁止充电,非0:充放电设备充电电流不能超过该值 if it's '0', the battery string can't be discharged and if other data is the max. charge current that the battery can be accepted
Charge power limits | [0,50000] | 0.1kW | PCS/中控必须监控；0:禁止充电,非0:充放电设备充电电流不能超过该值 if it's '0', the battery string can't be charged and if other data is the max. charge power that the battery can be accepted
Discharge power limits | [0,50000] | 0.1kW | PCS/中控必须监控；0:禁止充电,非0:充放电设备充电电流不能超过该值 if it's '0', the battery string can't be discharged and if other data is the max. charge power that the battery can be accepted

## alarm bits
Battery string external alarm information 0
序号(bit) | 含义Explain | 格式Format
0 | 1#电池组充电过流Battery string charge over current | '0':normal ; '1':alarm
1 | 1#电池组放电过流Battery string discharge over current | '0':normal ; '1':alarm
2 | 1#电池组电池过压Battery string charge high voltage | '0':normal ; '1':alarm
3 | 1#电池组电池欠压Battery string discharge low voltage | '0':normal ; '1':alarm
4 | 1#电池组电池过温Battery string high temperature | '0':normal ; '1':alarm
5 | 1#电池组电池低温Battery string low temperature | '0':normal ; '1':alarm
6 | 1#电池组隔离开关断开Battery string DC-switch cutoff | '0':normal ; '1':alarm
7 | 1#电池组预留开关1断开Battery string switch1 cutoff(reserve) | '0':normal ; '1':alarm
8 | 1#电池组预留开关2断开Battery string switch2 cutoff(reserve) | '0':normal ; '1':alarm
9 | 1#电池组高压采样异常Battery string high voltage sampling alarm | '0':normal ; '1':alarm
10 | 1#电池组高压端温度采样异常Control box temperature sampling alarm | '0':normal ; '1':alarm
11 | 1#电池组漏电检测失效Control box high voltage leak current sampling alarm | '0':normal ; '1':alarm
12 | 1#电池组预充过温Control box pre-charge circuit over temperature | '0':normal ; '1':alarm
13 | 1#电池组接触器过温Control box relaies over temperature | '0':normal ; '1':alarm
14 | 1#电池组熔断器过温Control box fuse over temperature | '0':normal ; '1':alarm
15 | 1#电池组启动失败Battery string start failure | '0':normal ; '1':alarm
Battery string external alarm information 1
序号(bit) | 含义Explain | 格式Format
0 | 1#电池组自行保护Battery string protected | '0':normal ; '1':alarm
1 | 1#电池组与高压检测模块通讯CAN断线Communication between Battery Module and control box is failure | '0':normal ; '1':alarm
2 | 1#电池组预留(reserve) | '0':normal ; '1':alarm
3 | 1#电池组预留(reserve) | '0':normal ; '1':alarm
4 | 1#电池组预留(reserve) | '0':normal ; '1':alarm
5 | 1#电池组预留(reserve) | '0':normal ; '1':alarm
6 | 1#电池组预留(reserve) | '0':normal ; '1':alarm
7 | 1#电池组预留(reserve) | '0':normal ; '1':alarm
8 | 1#电池组预留(reserve) | '0':normal ; '1':alarm
9 | 1#电池组预留(reserve) | '0':normal ; '1':alarm
10 | 1#电池组预留(reserve) | '0':normal ; '1':alarm
11 | 1#电池组预留(reserve) | '0':normal ; '1':alarm
12 | 1#电池组预留(reserve) | '0':normal ; '1':alarm
13 | 1#电池组预留(reserve) | '0':normal ; '1':alarm
14 | 1#电池组预留(reserve) | '0':normal ; '1':alarm
15 | 1#电池组预留(reserve) | '0':normal ; '1':alarm
Battery string internal alarm information 0
序号(bit) | 含义Explain | 格式Format
0 | 1#电池组充电电流超限值The charge current is larger than the limits | '0':normal ; '1':alarm
1 | 1#电池组放电电流超限值The discharge current is larger than the limits | '0':normal ; '1':alarm
2 | 1#电池组充电严重过流The charge current is serious larger than the limits | '0':normal ; '1':alarm
3 | 1#电池组放电严重过流The discharge current is serious larger than the limits | '0':normal ; '1':alarm
4 | 1#电池组严重高压The battery string voltage is serious higher than the limits | '0':normal ; '1':alarm
5 | 1#电池组严重低压The battery string voltage is serious lower than the limits | '0':normal ; '1':alarm
6 | 1#电池组严重低温The battery string temperature is serious lower than the limits | '0':normal ; '1':alarm
7 | 1#电池组电压一致性下降The cell voltage consistency is poor | '0':normal ; '1':alarm
8 | 1#电池组温场分布不均The temperature difference of each part of the battery string is too large | '0':normal ; '1':alarm
9 | 1#电池组容量衰减异常The capacity reduce abnormal | '0':normal ; '1':alarm
10 | 1#电池组剩余容量低SOC is low | '0':normal ; '1':alarm
11 | 1#电池组预留(reserve) | '0':normal ; '1':alarm
12 | 1#电池组预留(reserve) | '0':normal ; '1':alarm
13 | 1#电池组预留(reserve) | '0':normal ; '1':alarm
14 | 1#电池组预留(reserve) | '0':normal ; '1':alarm
15 | 1#电池组预留(reserve) | '0':normal ; '1':alarm
Battery string internal alarm information 1
序号(bit) | 含义Explain | 格式Format
0 | 1#电池组BMU均衡回检电路异常BMU cell balance confirm signal abnormal | '0':normal ; '1':alarm
1 | 1#电池组BMU均衡控制电路异常BMU cell balance control signal abnormal | '0':normal ; '1':alarm
2 | 1#电池组预留(reserve) | '0':normal ; '1':alarm
3 | 1#电池组预留(reserve) | '0':normal ; '1':alarm
4 | 1#电池组预留(reserve) | '0':normal ; '1':alarm
5 | 1#电池组预留(reserve) | '0':normal ; '1':alarm
6 | 1#电池组预留(reserve) | '0':normal ; '1':alarm
7 | 1#电池组BMU软件版本异常BMU software version abnormal | '0':normal ; '1':alarm
8 | 1#电池组单体电压偏高预警Cell voltage high alarm | '0':normal ; '1':alarm
9 | 1#电池组单体电压偏低预警Cell voltage low alarm | '0':normal ; '1':alarm
10 | 1#电池组保留(reserve) | '0':normal ; '1':alarm
11 | 1#电池组保留(reserve) | '0':normal ; '1':alarm
12 | 1#电池组保留(reserve) | '0':normal ; '1':alarm
13 | 1#电池组保留(reserve) | '0':normal ; '1':alarm
14 | 1#电池组保留(reserve) | '0':normal ; '1':alarm
15 | 1#电池组保留(reserve) | '0':normal ; '1':alarm

## fault bits
Battery string external fault information 0
序号(bit) | 含义Explain | 格式Format
0 | 1#电池组BMU采样电路异常BMU cell voltage sampling error | '0':normal ; '1':fault
1 | 1#电池组BMU采样线断线BMU cell voltage sampling break line | '0':normal ; '1':fault
2 | 1#电池组内部与BMU通讯CAN断线CAN communication between BMUs is failure | '0':normal ; '1':fault
3 | 1#电池组外部与BSMU通讯CAN断线CAN communication between BCMU and BSMU is failure | '0':normal ; '1':fault
4 | 1#电池组电流采样电路异常Battery string curren sampling error | '0':normal ; '1':fault
5 | 1#电池组接触器回检电路异常Relaies' confirm signals error in ontrol box | '0':normal ; '1':fault
6 | 1#电池组熔断器熔断Fuse tripped in ontrol box | '0':normal ; '1':fault
7 | 1#电池组烟雾传感器报警Smoke sensor alarm(reserve) | '0':normal ; '1':fault
8 | 1#电池组漏电Control box high voltage leak current is larger than limits | '0':normal ; '1':fault
9 | 1#电池组严重过温保护Cell temperature serious high protection | '0':normal ; '1':fault
10 | 1#电池组电池单体失效Cell voltage failure | '0':normal ; '1':fault
11 | 1#电池组负极接触器异常Negative relay abnormal in control box(reserve) | '0':normal ; '1':fault
12 | 1#电池组主接触器异常Main relay abnormal in control box | '0':normal ; '1':fault
13 | 1#电池组预充接触器异常Pre-charge relay abnormal in control box | '0':normal ; '1':fault
14 | 1#电池组预留(reserve) | '0':normal ; '1':fault
15 | 1#电池组预留(reserve) | '0':normal ; '1':fault
Battery string external fault information 1
序号(bit) | 含义Explain | 格式Format
0 | 1#电池组预留(reserve) | '0':normal ; '1':fault
1 | 1#电池组预留(reserve) | '0':normal ; '1':fault
2 | 1#电池组预留(reserve) | '0':normal ; '1':fault
3 | 1#电池组预留(reserve) | '0':normal ; '1':fault
4 | 1#电池组预留(reserve) | '0':normal ; '1':fault
5 | 1#电池组预留(reserve) | '0':normal ; '1':fault
6 | 1#电池组预留(reserve) | '0':normal ; '1':fault
7 | 1#电池组预留(reserve) | '0':normal ; '1':fault
8 | 1#电池组预留(reserve) | '0':normal ; '1':fault
9 | 1#电池组预留(reserve) | '0':normal ; '1':fault
10 | 1#电池组预留(reserve) | '0':normal ; '1':fault
11 | 1#电池组预留(reserve) | '0':normal ; '1':fault
12 | 1#电池组预留(reserve) | '0':normal ; '1':fault
13 | 1#电池组预留(reserve) | '0':normal ; '1':fault
14 | 1#电池组预留(reserve) | '0':normal ; '1':fault
15 | 1#电池组预留(reserve) | '0':normal ; '1':fault
Battery string internal fault information 0
序号(bit) | 含义Explain | 格式Format
0 | 1#电池组严重漏电Control box high voltage leak current is serious larger than limits | '0':normal ; '1':fault
1 | 1#电池组负极接触器回检电路异常Negative relay abnormal in control box(reserve) | '0':normal ; '1':fault
2 | 1#电池组主接触器回检电路异常Main relay abnormal in control box | '0':normal ; '1':fault
3 | 1#电池组预充接触器回检电路异常Pre-charge relay abnormal in control box | '0':normal ; '1':fault
4 | 1#电池组预留(reserve) | '0':normal ; '1':fault
5 | 1#电池组预留(reserve) | '0':normal ; '1':fault
6 | 1#电池组预留(reserve) | '0':normal ; '1':fault
7 | 1#电池组预留(reserve) | '0':normal ; '1':fault
8 | 1#电池组预留(reserve) | '0':normal ; '1':fault
9 | 1#电池组预留(reserve) | '0':normal ; '1':fault
10 | 1#电池组预留(reserve) | '0':normal ; '1':fault
11 | 1#电池组预留(reserve) | '0':normal ; '1':fault
12 | 1#电池组预留(reserve) | '0':normal ; '1':fault
13 | 1#电池组预留(reserve) | '0':normal ; '1':fault
14 | 1#电池组预留(reserve) | '0':normal ; '1':fault
15 | 1#电池组预留(reserve) | '0':normal ; '1':fault
Battery string internal fault information 1
序号(bit) | 含义Explain | 格式Format
0 | 1#电池组BMU采样电路异常BMU cell voltage sampling error | '0':normal ; '1':fault
1 | 1#电池组BMU电压采样线断线BMU cell voltage sampling break line | '0':normal ; '1':fault
2 | 1#电池组BMU温度采样线断线BMU cell temperature sampling break line | '0':normal ; '1':fault
3 | 1#电池组预留(reserve) | '0':normal ; '1':fault
4 | 1#电池组预留(reserve) | '0':normal ; '1':fault
5 | 1#电池组预留(reserve) | '0':normal ; '1':fault
6 | 1#电池组预留(reserve) | '0':normal ; '1':fault
7 | 1#电池组预留(reserve) | '0':normal ; '1':fault
8 | 1#电池组BMU内部CAN断线CAN communication between BMUs is failure | '0':normal ; '1':fault
9 | 1#电池组预留(reserve) | '0':normal ; '1':fault
10 | 1#电池组预留(reserve) | '0':normal ; '1':fault
11 | 1#电池组预留(reserve) | '0':normal ; '1':fault
12 | 1#电池组预留(reserve) | '0':normal ; '1':fault
13 | 1#电池组预留(reserve) | '0':normal ; '1':fault
14 | 1#电池组预留(reserve) | '0':normal ; '1':fault
15 | 1#电池组预留(reserve) | '0':normal ; '1':fault

## IO status
电池组输出IO状态:Battery string output status/Control box switches status
序号(bit) | 含义Explain | 格式Format
0 | 负极接触器状态Negative relay status | '0':disconnect/cutoff ; '1'：connect/closed
1 | 主接触器状态Main relay status | '0':disconnect/cutoff ; '1'：connect/closed
2 | 预充接触器状态Pre-charge relay status | '0':disconnect/cutoff ; '1'：connect/closed
3 | 保留(reserve) | '0':disconnect/cutoff ; '1'：connect/closed
4 | 保留(reserve) | '0':disconnect/cutoff ; '1'：connect/closed
5 | 保留(reserve) | '0':disconnect/cutoff ; '1'：connect/closed
6 | 保留(reserve) | '0':disconnect/cutoff ; '1'：connect/closed
7 | 保留(reserve) | '0':disconnect/cutoff ; '1'：connect/closed
8 | 保留(reserve) | '0':disconnect/cutoff ; '1'：connect/closed
9 | 保留(reserve) | '0':disconnect/cutoff ; '1'：connect/closed
10 | 保留(reserve) | '0':disconnect/cutoff ; '1'：connect/closed
11 | 保留(reserve) | '0':disconnect/cutoff ; '1'：connect/closed
12 | 保留(reserve) | '0':disconnect/cutoff ; '1'：connect/closed
13 | 保留(reserve) | '0':disconnect/cutoff ; '1'：connect/closed
14 | 保留(reserve) | '0':disconnect/cutoff ; '1'：connect/closed
15 | 保留(reserve) | '0':disconnect/cutoff ; '1'：connect/closed
电池组输入IO状态:Battery string output status/Control box switches status
序号(bit) | 含义Explain | 格式Format
0 | 保留(reserve) | '0':disconnect/cutoff ; '1'：connect/closed
1 | 保留(reserve) | '0':disconnect/cutoff ; '1'：connect/closed
2 | 保留(reserve) | '0':disconnect/cutoff ; '1'：connect/closed
3 | 保留(reserve) | '0':disconnect/cutoff ; '1'：connect/closed
4 | 保留(reserve) | '0':disconnect/cutoff ; '1'：connect/closed
5 | 保留(reserve) | '0':disconnect/cutoff ; '1'：connect/closed
6 | 保留(reserve) | '0':disconnect/cutoff ; '1'：connect/closed
7 | 保留(reserve) | '0':disconnect/cutoff ; '1'：connect/closed
8 | 保留(reserve) | '0':disconnect/cutoff ; '1'：connect/closed
9 | 保留(reserve) | '0':disconnect/cutoff ; '1'：connect/closed
10 | 保留(reserve) | '0':disconnect/cutoff ; '1'：connect/closed
11 | 保留(reserve) | '0':disconnect/cutoff ; '1'：connect/closed
12 | 保留(reserve) | '0':disconnect/cutoff ; '1'：connect/closed
13 | 保留(reserve) | '0':disconnect/cutoff ; '1'：connect/closed
14 | 保留(reserve) | '0':disconnect/cutoff ; '1'：connect/closed
15 | 保留(reserve) | '0':disconnect/cutoff ; '1'：connect/closed